## Note
NOTE:
1. | LOCATION Tab |  | 3. | Auxiliary Instrument
| Field | Field/Площадка |  | P | Surge Protector
| DCS | DCS Control System |  | B | Safety Barrier
| SIS | SIS Control System |  | I | Isolator
| GDS | GDS Control System |  | D | Signal Splitter
| ITCC | ITCC Control System |  | R | Relay
| MMS | Machinery Monitoring System
| MCC | Motor control System
| AUX | Control Console
| LCP | Local Control Panel
2. | IO Type Tab
| TC | Thermocouple（IEC Standard）
| HART | HART Communicate
| DI-VFC | Digital Input(votage free contact)
| DI-NAMUR | Digital Input(NAMUR)
| DI-COM | Digital Input(Communicate,eg: Modbus-TCP)
| DO-VFC | Digital Output(votage free contact)
| DO-P | Digital Output(24VDC)
| DO-COM | Digital Output(Communicate,eg: Modbus-TCP)
| AI-LP | 4-20mA Analog Input（Loop power）
| AI-EP | 4-20mA Analog Input（Extra power）
| AI-COM | Analog Input(Communicate,eg: RS485)
| AO | 4-20mA Analog Output
| AO-COM | Analog Output(Communicate,eg: RS485)
| R | Redundant signal
| (I) | Intrinsically Safe Signal
| S | Soft signal in control system

## GDS
Title | Loop No. | Logic No. | Tag No. | Service | Instrument Type | PID No. | Location | I/O Type | Ex.type | System | Sub System | Auxiliary Instrument P/B/I/D/R | Instrument Range |  |  | System Range |  |  | Alarm & Interlock Setpoint |  |  |  |  | Rev. | Remarks
[13 empty] | Min | Max | Unit | Min | Max | Unit | LL | L | H | HH | Unit |  |  | Logic No.
1702 | 2712-G-3001 | Z-00111/00112 | 2712-GMCT-3001 | Unit 1702 2712-PK-0001 Styrene & Ethylbenzene | Combustible Gas Detector | NKNH21002-1702-ATX.DW-0001 | Field | AIR-EP(3 WIRES) | Ex.d | GDS | - | - | 0 | 100 | %LEL | 0 | 100 | %LEL | - | - | 10 | 20 | %LEL | 0 | - | Z-00111/00112
- | - | - | - | - | - | - | - | - | - | - | - | - | [11 empty] | - | - | bar: Instrument Range Min to Alarm & Interlock Setpoint Unit
1702 | 2712-G-3002 | Z-00111 | 2712-GMCT-3002 | Unit 1702 Styrene & Ethylbenzene | Combustible Gas Detector | NKNH21002-1702-ATX.DW-0001 | Field | AIR-EP(3 WIRES) | Ex.d | GDS | - | - | 0 | 100 | %LEL | 0 | 100 | %LEL | - | - | 10 | 20 | %LEL | 0 | - | Z-00111
- | - | - | - | - | - | - | - | - | - | - | - | - | [11 empty] | - | - | bar: Instrument Range Min to Alarm & Interlock Setpoint Unit
1702 | 2712-G-3003 | Z-00112 | 2712-GMCT-3003 | Unit 1702 Loading Crane Styrene & Ethylbenzene | Combustible Gas Detector | NKNH21002-1702-ATX.DW-0001 | Field | AIR-EP(3 WIRES) | Ex.d | GDS | - | - | 0 | 100 | %LEL | 0 | 100 | %LEL | - | - | 10 | 20 | %LEL | 0 | - | Z-00112
- | - | - | - | - | - | - | - | - | - | - | - | - | [11 empty] | - | - | bar: Instrument Range Min to Alarm & Interlock Setpoint Unit
1702 | 2712-G-3004 | Z-00111/00112 | 2712-GMCT-3004 | Unit 1702 2712-V-0001 Styrene & Ethylbenzene | Combustible Gas Detector | NKNH21002-1702-ATX.DW-0001 | Field | AIR-EP(3 WIRES) | Ex.d | GDS | - | - | 0 | 100 | %LEL | 0 | 100 | %LEL | - | - | 10 | 20 | %LEL | 0 | - | Z-00111/00112
- | - | - | - | - | - | - | - | - | - | - | - | - | [11 empty] | - | - | bar: Instrument Range Min to Alarm & Interlock Setpoint Unit
1702 | 2712-B-0003 | - | 2712-BIALS-0003 | Combustible Gas Alarm in Unit 1702 | Horn and Light Alarm | NKNH21002-1702-ATX.DW-0001 | Field | DOR-P | Ex.d | GDS | - | R | [11 empty] | 0 | - | bar: Instrument Range Min to Alarm & Interlock Setpoint Unit
- | - | - | - | - | - | - | - | - | - | - | - | - | [11 empty] | - | - | bar: Instrument Range Min to Alarm & Interlock Setpoint Unit
1702 | - | Z-00111/00112 | 2712-GZY-00111 | GDS Interlock to SIS | Relay Contact | - | SIS | DOR-VFC | - | GDS | - | R | [11 empty] | 1 | Rev1 New add | Z-00111/00112 | bar: Instrument Range Min to Alarm & Interlock Setpoint Unit